Mt. Morgan SITE WORK INSTRUCTION

Water Treatment Plant Feed and Discharge Sampling

Standard Work Instruction  ·  Heritage Minerals  ·  Mt. Morgan Processing Plant

| Document number | SWI-PRO-MET-201-019 |
| --- | --- |
| JSEA reference | JSEA-PRO-MET-201-019 |
| Area | 092 / 093 Water Treatment |
| Parent procedure | HM-PRC-VXX-PRO205 Plant Sampling and Metallurgical Data Collection |
| Classification | Safety-critical |
| Revision | Rev A |
| Date | 11 August 2026 |
| Prepared by | GGT (cost code 4034-033) |
| Reviewed by | ________________________ |
| Approved by | ________________________ |

ISSUED BUT NOT FOR USE. Part A (water treatment plant No. 1 and No. 2 feed and discharge) still cannot be completed - the circuit narrative is missing, see the folder README. Part B is a Martabe water-filter sampling technique from 'Sampling Raw and Filtrat Water' (DOC-3-MET-PRS-WIN-00063-IE), added as a draft technique reference only. It is for a potable water filter, not for the discharge that carries the licence obligation.

# 1  TASK AND SCOPE

Set the feed and discharge quality across the water treatment plant.

Discharge quality carries the environmental licence obligation.

Points and equipment covered:

| Tag / point | Description |
| --- | --- |
| 092 | Water treatment plant No. 1 - feed and discharge |
| 093 | Water treatment plant No. 2 - feed and discharge |

Frequency: To be set once the circuit narrative is available.

This instruction sits under Standard Work Procedure HM-PRC-VXX-PRO205 - Plant Sampling and Metallurgical Data Collection. Read that procedure before carrying out this task for the first time.

Register line: SWI-PRO-MET-201-019 in HM-MMM-WHS-REG-XXX-R00-SWI-SWMS, tab SWI-MET. The matching hazard analysis is JSEA-PRO-MET-201-019.

# 2  WHO MAY DO THIS

- Trained and signed off against this instruction.

- Signed on to JSEA JSEA-PRO-MET-201-019 at a communication session.

- Site inducted, with current cyanide awareness and gas detection competency where the area requires it.

- Authorised by the Shift Supervisor before the task starts.

This is a safety-critical task. It is not carried out alone in a cyanide area, and not without the Shift Supervisor knowing it is in progress.

# 3  HAZARDS SPECIFIC TO THIS TASK

| Hazard | Control |
| --- | --- |
| Hydrogen cyanide gas released at the open sample point | Personal HCN monitor worn and switched on, in calibration date. Fixed detection confirmed healthy - alarm 5 ppm, high-high 10 ppm. Sample point approached from upwind. pH of the stream confirmed above 10.5 before opening. Second person in sight and clear. Cyanide antidote kit on site and a trained first aider on shift. Withdraw upwind and report on any reading above the site action level. |
| Splash of cyanide-bearing slurry or solution to skin or eyes | Sample valve opened slowly with the container positioned first and the body out of the spray path. Face shield, chemical splash goggles, chemical-resistant gloves and apron. Never open a sample valve whose discharge cannot be seen. Safety shower and eyewash proven flowing before the round starts. |
| Slip, trip or fall on wet or slurry-covered walkways around sample points | Spillage cleaned up immediately and the point left clean. Walkways kept clear of hoses, buckets and containers. Safety boots with sound tread. Report any damaged or missing grating before use. |
| Non-representative sample leading to a wrong process decision | Line flushed for the stated time before collecting. Sample taken at the same point, in the same way and at the same frequency every time. Container labelled BEFORE the sample is taken, with point, date, time and shift. Steady-state confirmed for 15 to 20 minutes before sampling. A sample taken off-condition is marked as such or discarded. |
| [JSEA to confirm] Water splash, wet floor and overhead pipes at a water filter sampling point | Latex gloves, glasses, hard hat and safety boots. Watch footing on wet floors. Watch overhead pipes and keep the hard hat on. Hold the bottle directly under the outflow. |

The full step-by-step hazard analysis, with the risk ranking, is in JSEA JSEA-PRO-MET-201-019 Section 4.

# 4  PPE

- Hard hat

- Safety glasses

- High-visibility long-sleeved shirt and long trousers

- Safety boots

- Gloves appropriate to the task

- Personal HCN gas monitor, calibrated and in test date

- Chemical splash goggles and face shield

- Nitrile rubber gloves

- Nitrile PVC boots

- Chemical resistant suit

- Full or half gas mask with A2B2E2K2P3 cartridge, carried and available for immediate use

# 5  BEFORE YOU START

Every item below must be true. If one is not, stop and report it.

- Confirm the plant is in steady-state operation - normal operation for a minimum of 15 to 20 minutes before sampling. A sample taken during a swing is not representative.

- Notify the control room or DCS operator that the sampling round is starting, and which points it covers.

- Confirm the personal gas monitor is on, in calibration date and reading clean, and that fixed detection in the area is healthy.

- Confirm the safety shower and eyewash nearest the point are within reach and proven flowing.

- Label every container BEFORE sampling - point, date, time and shift.

- Rinse the container, cutter or sieve with process water and then with the stream being sampled. Discard the rinse.

Equipment required:

- To be confirmed once the plant configuration is known

# 6  STEPS

Part A - Water treatment plant No. 1 and No. 2 feed and discharge

1.  This instruction cannot be completed. See the hold below.

2.  The document is issued so the register line is not empty, and is marked NOT FOR USE.

Part B - Raw and filtrate water sampling technique at a water filter [M]

[M] = taken from the Martabe team work instruction "Sampling Raw and Filtrat Water (DOC-3-MET-PRS-WIN-00063-IE)" (25/12/2024). [CONFIRM] = unspecified or inconsistent in the source; resolve before this instruction is approved for use.

[CONFIRM] the source is for the Martabe potable water filter (raw water in, filtrate out), not for water treatment plant No. 1 or No. 2 feed and discharge. 'SLS' and the assay suite are not defined. Use it only as a sampling technique until the circuit narrative arrives. Cyanide-bearing water needs the Section 3 controls, not this part alone.

3.  Take 5 minutes before starting ('Take 5'). Prepare 1 L sample bottles. Make sure the filter plant is running in its filtration sequence [M].

4.  Raw (input) water: the sampling point is next to the vertical SLS ladder. Stand so you are not under the sampling point.

5.  Open the tap upward slowly and wait about 30 to 60 seconds so the sample is representative. Rinse the bottle with raw water.

6.  Hold the bottle right under the outflow and wait until it is full. Collect at least 900 mL.

7.  Close the tap downward. Make sure no water is still coming out of the tap.

8.  Filtrate water: the sampling point is below the raw water point. Take the sample with the same steps.

9.  Send the samples to the laboratory for assay (the source says ITS) and record the result in 'G:\Processing\5. Metallurgy\Metallurgy\34. Water\Assay sample Potable Water Final.xlsb'.

# 7  ON COMPLETION

- Close the sample valve or stop the sample pump and confirm the point is not weeping.

- Wash down the point and the surrounding walkway. Leave nothing on the grating.

- Record sampling time, operator name and the operating conditions read at the time - flow, density and any instrument value available.

- Deliver the labelled samples to the laboratory or to the composite station as the schedule requires, and sign the handover.

- Notify the control room that the round is complete.

# 8  RECORDS

- Field or bench data sheet - date, time, shift, operator, and every value determined.

- Register or logbook entry and any handover signature.

- Any step not completed, recorded with the reason.

- Any control in Section 3 found not in place, reported to the Shift Supervisor and recorded.

# 9  REFERENCE

- No source held

- Martabe work instruction 'Sampling Raw and Filtrat Water' DOC-3-MET-PRS-WIN-00063-IE v1.0 (issued 25/12/2024) - Part B sampling technique