Safe Work Instruction

Water Treatment Plant Feed and Discharge Sampling

This document is the property of Heritage Minerals with all rights are reserved in respect of it. This document cannot be reproduced without the written consent of Heritage Minerals

# Purpose and Scope

This Safe Work Instruction is required so that the mechanical and operational integrity of the system is kept intact. It assists operators and mechanical technicians alike to identify possible problems before they happen.  It will help ensure that when personnel are performing this task it is performed in a safe and secure manner, to ensure the operational integrity of the machine and applies when this task is performed either by itself or in conjunction with other tasks in the area.

A JSA or Take 5 must be completed and discussed with the Supervisor if any variation to this SWI is necessary.

# RESPONSIBILITIES AND AUTHORITY

| What | Who | When |
| --- | --- | --- |
| Conform to procedure: Implement Changes: Change procedure: Review: Authorisation: | All personnel Anyone Training Facilitator Working party of content experts Manager | At all times As required As required On change & yearly On change |

# PPE REQUIREMENTS

- Safety helmet and safety glasses

- Chemical splash goggles and face shield

- High-visibility long-sleeved shirt and long trousers

- Safety boots with sound tread - nitrile PVC boots at the sample point

- Chemical resistant suit, nitrile rubber gloves and apron

- Personal HCN gas monitor, calibrated and in test date

- Full or half gas mask with A2B2E2K2P3 cartridge, carried and available for immediate use

In the event of an emergency

Call on CH19 “EMERGENCY, EMERGENCY, EMERGENCY” on the project to make everyone aware, call 000 for emergency services, police, fire or ambulance, you will need to stay calm and state when requested by a responder:

• Your Name. • Your Location. • Type of Emergency; and • Assistance Required.

| Part 1: Information |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Title: |  |  | SWI-PRO-MET-201-019 - Water Treatment Plant Feed and Discharge Sampling |  |  |  |  |  |  |  |  |  |  |  |
| Issued Date: |  |  | 11/08/2026 |  |  |  |  | Next Review Date: |  |  |  | 11/08/2027 |  |  |
| Document Owner: |  |  | Processing |  |  |  |  | JSEA ID: |  |  |  | JSEA-PRO-MET-201-019 |  |  |
| Part 2: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Description of work: |  |  |  |  |  | Set the feed and discharge quality across the water treatment plant. Discharge quality carries the environmental licence obligation. Check the raw (input) water and the filtrate water at the water filter, using the sampling technique in Steps 2 and 3. Area: 092 / 093 Water Treatment. Points and equipment covered: 092 - Water treatment plant No. 1, feed and discharge 093 - Water treatment plant No. 2, feed and discharge Water filter - raw (input) water and filtrate water Frequency: To be set. Note: the sampling points need to be updated. The points for water treatment plant No. 1 and No. 2 feed and discharge, and for the raw and filtrate water, are to be confirmed against the plant. The sampling technique in Steps 2 and 3 is taken from the Martabe work instruction Sampling Raw and Filtrat Water (DOC-3-MET-PRS-WIN-00063-IE, v1.0, 25/12/2024), where the raw water point is next to the vertical SLS ladder and the filtrate point is below it. The assay suite and the laboratory are to be set. JSEA-PRO-MET-201-019 must be updated for the added hazard. This is a safety-critical task. It is not carried out alone in a cyanide area, and not without the Shift Supervisor knowing it is in progress. |  |  |  |  |  |  |  |  |
| Potential Hazards: |  |  |  |  |  | Hydrogen cyanide gas released at the open sample point — Personal HCN monitor worn and switched on, in calibration date. Fixed detection confirmed healthy - alarm 5 ppm, high-high 10 ppm. Sample point approached from upwind. pH of the stream confirmed above 10.5 before opening. Second person in sight and clear. Cyanide antidote kit on site and a trained first aider on shift. Withdraw upwind and report on any reading above the site action level. Splash of cyanide-bearing slurry or solution to skin or eyes — Sample valve opened slowly with the container positioned first and the body out of the spray path. Face shield, chemical splash goggles, chemical-resistant gloves and apron. Never open a sample valve whose discharge cannot be seen. Safety shower and eyewash proven flowing before the round starts. Slip, trip or fall on wet or slurry-covered walkways around sample points — Spillage cleaned up immediately and the point left clean. Walkways kept clear of hoses, buckets and containers. Safety boots with sound tread. Report any damaged or missing grating before use. Non-representative sample leading to a wrong process decision — Line flushed for the stated time before collecting. Sample taken at the same point, in the same way and at the same frequency every time. Container labelled BEFORE the sample is taken, with point, date, time and shift. Steady-state confirmed for 15 to 20 minutes before sampling. A sample taken off-condition is marked as such or discarded. [JSEA to confirm] Water splash, wet floor and overhead pipes at a water filter sampling point — Latex gloves, glasses, hard hat and safety boots. Watch footing on wet floors. Watch overhead pipes and keep the hard hat on. Hold the bottle directly under the outflow. The full step-by-step hazard analysis, with the risk ranking, is in JSEA-PRO-MET-201-019 Section 4. |  |  |  |  |  |  |  |  |
| PERSONAL PROTECTIVE EQUIPMENT (PPE): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Part 3: Safe Work Instruction Steps |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Job Number (Hazards/Cautions) |  | Application Method |  |  |  |  |  |  | Visual Reference |  |  |  |  |  |
| - Pre-start Check - Working alone in a cyanide area - Gas monitor or fixed detection not healthy - Safety shower or eyewash not proven flowing - Filter plant not in its filtration sequence |  | - Confirm you are trained and signed off against this SWI, signed on to JSEA-PRO-MET-201-019 at a communication session, site inducted with current cyanide awareness and gas detection competency where the area requires it, and authorised by the Shift Supervisor. - Confirm a second person is in the area. Cyanide-area sampling is not done alone. - Take 5 minutes before starting (Take 5). Prepare 1 L sample bottles. - Make sure the filter plant is running in its filtration sequence. - Confirm the plant is in steady-state operation - normal operation for a minimum of 15 to 20 minutes before sampling. A sample taken during a swing is not representative. - Notify the control room or DCS operator that the sampling round is starting, and which points it covers. - Confirm the personal gas monitor is on, in calibration date and reading clean, and that fixed detection in the area is healthy. - Confirm the safety shower and eyewash nearest the point are within reach and proven flowing. - Label every container BEFORE sampling - point, date, time and shift. - Rinse the container, cutter or sieve with process water and then with the stream being sampled. Discard the rinse. Equipment Required : - 1 L sample bottles - Other equipment to be confirmed once the plant configuration is known - Personal protective equipment as listed in PPE Requirements |  |  |  |  |  |  |  |  |  |  |  |  |
| - Raw (Input) Water Sampling - Water splash and wet floor - Overhead pipes - Sample not representative - HCN released from cyanide-bearing water |  | - Go to the raw water sampling point (to be updated). Stand so you are not under the sampling point. - Open the tap upward slowly and wait about 30 to 60 seconds so the sample is representative. Rinse the bottle with raw water. - Hold the bottle right under the outflow and wait until it is full. Collect at least 900 mL. - Close the tap downward. Make sure no water is still coming out of the tap. CAUTION: Watch footing on wet floors and watch overhead pipes with the hard hat on. Water from the treatment circuit can carry cyanide, so the HCN controls in Part 2 apply. |  |  |  |  |  |  |  |  |  |  |  |  |
| - Filtrate Water Sampling - Water splash and wet floor - Raw and filtrate samples swapped |  | - Go to the filtrate water sampling point, below the raw water point (to be updated). - Take the sample with the same steps as for the raw water. |  |  |  |  |  |  |  |  |  |  |  |  |
| - Dispatch and Records - Samples not traceable - Result not recorded |  | - Send the samples to the Mt. Morgan laboratory for assay. - Record the result in G:\\Processing\\5. Metallurgy\\Metallurgy\\34. Water\\Assay sample Potable Water Final.xlsb. |  |  |  |  |  |  |  |  |  |  |  |  |
| - Completion and Clean Up - Sample valve left weeping - Samples not handed over with a signed record - Control room not told the round is complete |  | - Close the sample valve or stop the sample pump and confirm the point is not weeping. - Wash down the point and the surrounding walkway. Leave nothing on the grating. - Record sampling time, operator name and the operating conditions read at the time - flow, density and any instrument value available. - Deliver the labelled samples to the laboratory or to the composite station as the schedule requires, and sign the handover. - Notify the control room that the round is complete. - Record the result, the method used and the instrument or balance identity on the field or bench data sheet - date, time, shift, operator and every value determined. Make the register or logbook entry and any handover signature. - Record any step not completed, with the reason. - Report to the Shift Supervisor, and record, any control in Part 2 found not in place. |  |  |  |  |  |  |  |  |  |  |  |  |

| Referenced Documents |  |
| --- | --- |
| Document ID | Document Title |
| JSEA-PRO-MET-201-019 | JSEA — Water Treatment Plant Feed and Discharge Sampling |
| DOC-3-MET-PRS-WIN-00063-IE v1.0 | Martabe WI Sampling Raw and Filtrat Water (25/12/2024) - source of Steps 2 and 3 |
| Note | No Mt. Morgan circuit source held for the water treatment plant - sampling points to be updated |

In the event of an emergency

1. HCN Gas Alarm If the personal monitor or fixed detection alarms (5 ppm alarm, 10 ppm high-high), stop work, leave the area upwind and call CH19 “EMERGENCY”. Do not re-enter until the Shift Supervisor clears the area. 2. Suspected Cyanide Exposure If a person becomes dizzy, short of breath or collapses, call CH19 “EMERGENCY”, call 000, and bring the cyanide antidote kit and a trained first aider. Do not give mouth-to-mouth resuscitation. 3. Skin or Eye Contact with Slurry Flush with copious water at the safety shower or eyewash for a minimum of 15 minutes. Remove contaminated clothing while flushing. Report to the first aider. 4. Slip, Fall or Lifting Injury Call CH19 “EMERGENCY”, call 000 if the injury is serious, and notify the Shift Supervisor.